## Slide 1: Various Methods for Attaining a Resilient and Secure Timing Architecture
Eran Gilat
Manager, Systems Architecture

## Slide 2: Agenda
  Resilient Global BMCA
  Majority Vote Algorithm
  Systems Redundancy Schemes
  Summary
Notes: In this presentation I’ll cover various methods attaining resilient and secure timing architecture using various signals of opportunity
1. Extension of BMCA and Alternate BMCA per IEEE1588 and ITU-T standards
3. Geographical redundancy / Active – Standby / Active –Active
4. Conclusion

## Slide 3: Resilient Global BMCA (G-BMCA) Algorithm
IEEE 1588 Definition:
The best master clock algorithm specifies the way that a PTP Instance determines which of all the PTP Instances (including itself) is the “best”
Advantages of G-BMCA
G-BMCA is an extension to the standard/alternate BMCA defined by IEEE 1588 and ITU-T standards Committee
Standard/alternate BMCA assume a single profile. G-BMCA can run with a mix of profiles using a mapping function of the various PTP parameters
In addition to the data set comparison, G-BMCA includes the comparison of PTP performance using a “Figure of Merit” metric
G-BMCA has the option to run on multiple clock domains to support parallel paths of synchronization (i.e., east/west domains) to protect against reference/path failures
G-BMCA
PTP
Input 1
PTP
Input 2
PTP
Input 3
PTP
Outputs
Notes: -G-BMCA is an extension of traditional BMCA in the extent of determination based on comparison of multiple PTP input against the local output
-While standard BMCA assumes single PTP profile, G-BMCA can run on various PTP profiles using a mapping function
-Figure of merit is based on Covariance function of Floor Percentile Population (F metrics
- G-BMCA can run on different domains

## Slide 4: Resilient Global BMCA Advantages
Compare
Clock Class
Compare DS of GM
A and B
Compare
Clock Accuracy
Compare
Clock Variance
Compare
Priority-2
Compare
Local Priority
Compare
Performance
Compare
Steps-removed
Ability to turn on/off “Performance” check
Conservative location of the “Performance” check in the G-BMCA chain
Future enhancements will include the ability to move the “Performance” check anywhere in the BMCA chain
Notes: Turn on and off and performance check
Performance check is placed in after local priority as a starting point.
Future – can control the performance check location

## Slide 5: Majority Vote Algorithm Essentials
Why?
  Security - spoofing attacks
  Resiliency - unintentional clock errors
What?
  Prior to the G-BMCA decision tree, Majority Vote (MV) can exclude any 1 of 3 time references
  MV determines if there are any outliers and rejects them
Supported Combinations:
  Three instances of PTP clients on the same system
  Two instances of PTP clients plus GNSS time reference
  Two instances of PTP clients plus G.8271 ToD time reference
G-BMCA
PTP
Input 1
PTP
Input 2
PTP
Input 3
Time
Outputs
ToD-1
GNSS
ToD-2
Majority Vote
Notes: In a nutshell - Majority vote is an option to further enhance G-BMCA with an algorithm supports “voting off the island” a spoofed ,jammed or unintentionally faulty signals.
What? Before G-BMCA is kicking in, Majority vote can exclude any outlier out of 3 time reference.
Supported combinations are..

## Slide 6: Majority Vote Algorithm–How?
Time offsets are calculated based on a single reference point
User defined threshold to determine correctness intervals
Dynamic adjustment of correctness intervals for hysteresis
Use a common algorithm to locate “Intersection Interval”
A change in state (reject or valid) will need to persist for few seconds before the change is reported
A
Time Offset
C
B
Example 1: Intersection of 3 clocks, all clocks are valid
Notes: User defined threshold to determine correctness intervals – (100ms for start)
Using a known algorithm to locate “intersection interval”
Persistence of few seconds in order to change a state

## Slide 7: Example 1–One Clock Outlier
Majority Vote Status
------------------------------------
| Reference | status |
|-------------------|--------------|
| GNSS | reject |
|...................|..............|
| PTP (PI-0) | valid |
|...................|..............|
| PTP (PI-1) | valid |
|...................|..............|
| PTP (PI-2) | not-used |
|...................|..............|
Unit Under Test (UUT) is initially locked to GNSS reference
Industry standard testing device is added into the scenario injecting arbitrary time with dual PTP references
UUT rejects the higher priority reference (GNSS)
Time Offset
PTP Client-1
PTP Client-2
GNSS
Alarm Status
-------------------------------------------------------------------------------------------------------------------
|ID |Severity|Date-Time |Description |
|---|--------|-------------------|--------------------------------------------------------------------------------|
|242|MINOR |2021-10-08 03:10:20|GNSS input reference majority vote rejection |
-------------------------------------------------------------------------------------------------------------------
| TOD-1 | not-used |
|...................|..............|
d |
------------------------------------
System Date and Time : 2021-10-08 02:00:32
Clock Time Status : LOCKED
Currently Selected Time Reference : PTP Client (PI-1)
Time State Duration (min) : 44
Clock Frequency Status : LOCKED
Currently Selected Frequency Reference : PTP Client (PI-1)
Frequency State Duration (min) : 48
System Uptime : 0 day(s) 1 hour(s) 7 minute(s) 4 second(s)
Timing Service Eth7 Mode : PTP Client (PI-0)
Timing Service Eth8 Mode : PTP Client (PI-1)
Timing Service Exp Mode : NONE
Active Management Interface : ETH1
Redundancy Mode Status : Stand-alone
Frequency Stability (MDEV ppb) : 0.114922
Phase Stability (TDEV ns) : 47.772
Active Alarms : 12
System Frequency PQL : 2
Operation Mode : gateway-clock
Last Config Time : 2021-10-10 05:25:29
System Status : ok
--------
Notes: Example 1 : Unit locked to GNSS, adding two Arbitrary time PTP feeds from a testing device
UUT rejects the GNSS reference with highest priority -> G-BMCA choose one of the PTP inputs

## Slide 8: Example 2–No Overlap
Majority Vote Status
------------------------------------
| Reference | status |
|-------------------|--------------|
| GNSS | valid |
|...................|..............|
| PTP (PI-0) | valid |
|...................|..............|
| PTP (PI-1) | valid |
|...................|..............|
| PTP (PI-2) | valid |
|...................|..............|
| TOD-1 | not-used |
|...................|..............|
| TOD-2 | not-used |
------------------------------------
Third PTP reference sourced from House Time Scale is added to the setup
There is no intersection, therefore majority vote cannot be determined. All clocks are marked valid
Higher priority was set to the GNSS input which is now selected as system reference
Time Offset
PTP Client-1
PTP Client-2
GNSS
|
------------------------------------
System Name : TimeProvider
Serial Number : SCA20070010F
System Date and Time : 2021-10-10 21:25:50
Clock Time Status : LOCKED
Currently Selected Time Reference : GNSS
Time State Duration (min) : 832
Clock Frequency Status : LOCKED
Currently Selected Frequency Reference : GNSS
Frequency State Duration (min) : 832
System Uptime : 0 day(s) 14 hour(s) 42 minute(s) 45 second(s)
Timing Service Eth1 Mode : NONE
Timing Service Eth2 Mode : NONE
Timing Service Eth3 Mode : NONE
Timing Service Eth4 Mode : NONE
Timing Service Eth5 Mode : PTP Client (PI-2)
Timing Service Eth6 Mode : NONE
Timing Service Eth7 Mode : PTP Client (PI-0)
Timing Service Eth8 Mode : PTP Client (PI-1)
Timing Service Exp Mode : NONE
Active Management Interface : ETH1
Redundancy Mode Status : Stand-alone
Frequency Stability (MDEV ppb) : 0.007607
Phase Stability (TDEV ns) : 3.162
Active Alarms : 0
System Frequency PQL : 1
Operation Mode : gateway-clock
Last Config Time : 2021-10-08 04:07:24
System Status : ok
Reference Criteria : priority
Reference Switch Mode : auto-return
Operation Mode : gateway-clock
Majority-Vote Mode : enable
Majority-Vote Threshold : 1000 ns
Time Reference Config
------------------------
| Reference | Priority |
|-----------|----------|
| GNSS | 1 |
|...........|..........|
| PTP | 2 |
|...........|..........|
| TOD-1 | 4 |
|...........|..........|
| TOD-2 | 4 |
------------------------
|
------------------------------------
PTP Client-3
Notes: Example 2 : a 3rd PTP input is added referenced from House time scale. 4 inputs / no majority since two groups disagree with each other -> system will go with highest priority input = GNSS in this example

## Slide 9: Introduction of Various Redundancy Schemes
Geographical Redundancy/Network Redundancy
Two or more PTP server units are deployed in separate locations in the network, same profile and same domain
According to BMCA or A-BMCA: PTP clients will connect to the lower priority GM in case of a fail-over scenario or attributes degradation
PTP server units are not synchronized and are not configured similarly. This is a plain fail-over network redundancy
PTP Client 1
PTP Client 1
PTP Client 3
PTP Client n

## Slide 10: Active Standby Redundancy
“Hardware Redundancy” achieved by using either:
  Two identical units, one is active, the other is standby
  Single redundant device with redundant clock modules
Behavior is essentially as a single unit
Out-of-Band channel for sync and management between redundant Hardware units
Both units have unified configuration, including software options
Unified PTP client list transferred via OOB channel
The two devices “look” like a single unit for all practical purposes and share the same GM Clock ID.
Unit management is only live for active units in case of dual hardware or is single connected via a non-redundant management module
PTP input is operative only on active units
PTP Client n
PTP Client 1
PTP Client 1
PTP Client 3
Management
PTP input
PTP input

## Slide 11: Active-Active Redundancy
  Two separate devices act as two separate GMs with Common Time Base
  Out of Band (OOB) channel is only for sync, not management
  Management is active on both units
  The two units are not necessarily configured similarly
  Much more flexibility but also potential risks for configuration errors
  PTP input or inputs available and active on both active units at the same time
  BMCA with Health status methods are used as arbitration method to determine SyncSender and SyncReceiver roles.
PTP Client n
PTP Client 1
PTP Client 1
PTP Client 3
Management
PTP input
PTP input

## Slide 12: Active-Active Redundancy (Contd.)
Active-Active redundancy is an extension of G-BMCA and Majority Vote features into hardware redundant platform
Determination of SyncSender and SyncReceiver roles takes advantage of either or both capabilities
Active-Active variant of redundancy allows support of additional architectures and use cases:
  Redundant SSU with Frequency only inputs
  vPRTC with mesh DWDM optical networks
PTP Client n
PTP Client 1
PTP Client 1
PTP Client 3
Management
PTP input
PTP input
G-BMCA
PTP
Input 1
PTP
Input 2
PTP
Input 3
PTP
Outputs

## Slide 13: Summary
There is a growing need in the industry to assure selected timing sources are valid and that the content isn’t spoofed or modified
IEEE 1588-2019 standard, under Security Annex P, introduced in Prong C Guidance to address security and resilience with architecture methods as described in this presentation
The use of techniques such as Global BMCA and Majority Vote are some of the methods being developed to ensure resilience timing performance
The Active-Active redundancy scheme is used to extend the reach of those techniques to support even more resiliency using 1:1 hardware redundancy

## Slide 14: Thank you
Eran Gilat
Manager, Systems Architecture
Eran.Gilat@microchip.com
Phone: +1-408-964-7671